| RELEASE NOTE |  |  |
| --- | --- | --- |
| Boss Order No.: 5032809 |  | DATE: 14.10.2021 |

| Name & Address of the Client | : | M/s. Goa Waste Management Corporation (GWMC) |
| --- | --- | --- |
| Name of the Project | : | MSW Treatment Facility of 100 TPD at Cacora in South Goa |
| Name & Address of the Manufacturer | : | Supplier - M/s. Vasudha Waste Treatment Pvt. Ltd. A/c. SFC Environmental Technologies Pvt. Ltd. Manufacturer – M/s. Intervalve Poonawalla Limited (Unit-1) 94/1 Manjri, Off Soli Poonawalla Road Pune 412307, India. |
| P/O No. & Date | : | PO No. SETPL/IVI/100 TPD SOUTH GOA/PO/20-21/029 Dated 14/05/2021 (M/s. SFC Environmental Technologies to M/s. Intervalve Poonawalla) |
| Date (s) & Place (s) of Inspection | : | On 06th October, 2021 at Manufacturers Work at Manjri, Hadapsar, Pune. |
| Description of Material | : | Valves |

| Item # as per Contract/ Order | Description & Size | Quantity as per Contract / Order (Nos.) | Quantity Previously passed (Nos.) | Quantity Offered (Nos.) | Quantity Now Passed (Nos.) | Quantity Rejected (Nos.) | Quantity Balance (Nos.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | M/s. Intervalve Poonawalla Make, Butterfly Valve & Check Valve Description, Size & Quantity Refer attached Annexure No.: B | -- | -- | -- | -- | -- | -- |

P.O. Status:  Balance

Form VF-IN-IND-IN-016                                             Ver: 1.1 /14.11.2020

| Boss Order No.: 5032809 | DATE: 14.10.2021 |
| --- | --- |

| Reference Document No. (Spec./ Standard / Code /Drawing / Sampling Standard / Any Other) | Scope of Inspection (Checks / Tests - witnessed & Reviewed) | Observation / Results |
| --- | --- | --- |
| PO No.: PO No. SETPL/IVI/100 TPD SOUTH GOA/PO/20-21/029 Dated 14/05/2021 (M/s. SFC Environmental Technologies to M/s. Intervalve Poonawalla) | - Review of Raw Materials test certificate/ compliance report for Body, Disc & Shaft - Review of Bought Out Items Raw Material test Certificate / Compliance Report for Seat & Hand Lever, Gear Box & Actuator Assembly - Quantity Verification of Offered Lot - Final Inspection - Completeness - Dimensional Check - Operation (Open/ Close) Witness - Hydro test for Shell Witness - Hydro Test for Seat Witness - Review of Painting Compliance Report | Satisfactory |
| QAP / ITP No.: VWT-SG100-ME-QP-145 |  |  |
| Approved Drawing No.: - PD57456/A (50, 80, 100, 125, 150mm Handlever Operated) - PD57457 (200mm worm Gear Box) - PD57458 (200mm Worm Gear Box) - PD57459 (250mm Work Gear Box) - PD57461 (100mm Pneumatic) - PD57460 ( 50 & 150mm Check Valve) Approved with comments by M/s. Vasudha Waste Treatment Pvt. Ltd.) |  |  |
| Reference Standards: As Per QAP & Drawings. |  |  |
| Sampling Standard: Edition/ Version/Year: As Per QAP RW 10% |  |  |

Sampling Standard 	: AS PER QAP

Identification 	:  ---

Remarks        		: This is a Final Inspection Report / Passed Quantity is cleared for dispatch.

Deviation accepted (if any):   NIL

| Inspection Identification | Location of Identification | Inspected By | Signature of SGS Representative |
| --- | --- | --- | --- |
| SGS Metal Punch As, SGS PN47 | SGS Hard Punch Stamp on witness qty. Single for Identification Purpose Only. | Dinesh Chaudhari |  |

The information stated in this release note is derived from the results of inspection or testing procedures carried out in accordance with the instructions of our clients, and / or our assessment of such results on the basis of any technical standards, trade custom or practice, or other circumstances which should in our professional opinion be taken into account.

“In accordance with Client’s instructions, the Company’s involvement has been limited to witnessing/observing a third party’s intervention(s) at the third party’s laboratory/test house or other facilities and installations used for the intervention(s). The Company’s sole responsibility was to be present at the time of the third party’s intervention(s) to forward the results, or confirm the occurrence, of the intervention(s). The Company is not responsible for the condition or calibration of apparatus, instruments and measuring devices used, the analysis methods applied the qualifications, actions or omissions of the third party’s personnel or the analysis results.

This document is issued by the Company under its General Conditions of Service accessible at http://www.sgs.com/terms_and_conditions.htm. Attention is drawn to the limitation of liability, indemnification and jurisdiction issues defined therein.   Any holder of this document is advised that information contained hereon reflects the Company’s findings at the time of it’s intervention only and within the limits of Client’s instructions, if any. The Company’s sole responsibility is to its client and this documents does not exonerate parties to a transaction from exercising all their rights and obligations under the transaction document.  Any unauthorized alteration, forgery or falsification of the content or appearance of this document is unlawful and offenders may be prosecuted to the fullest extent of the law”.

This inspection has been carried out to the best of our knowledge & our responsibility is limited to the exercise of reasonable care. This Release / Discrepancy Note reflects our findings at the time & place of inspection and is not intended to relieve the seller from their contractual obligations.

Form VF-IN-IND-IN-016 Ver: 1.1 /14.11.2020

for SGS India Private Limited

Annexure No.: B

| Item # as per Contract/ Order | Description & Size | Quantity as per Contract / Order (Nos.) | Quantity Previously passed (Nos.) | Quantity Offered (Nos.) | Quantity Now Passed (Nos.) | Quantity Rejected (Nos.) | Quantity Balance (Nos.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 & 2 | BUTTERFLY VALVE / 50 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF8 / EPDM / A479 TYPE 410 / HAND LEVER 7 NOTCHES Sr. No. 9999777733 to 9999777737 Witness Sr. No. 9999777734 | 5 | NIL | 5 | 5 | NIL | NIL |
| 3 to 8 | BUTTERFLY VALVE / 80 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY / A351 CF8 / EPDM / A479 TYPE 410 / HAND LEVER 7 NOTCHES Sr. No. 9999777738 to 9999777746 Witness Sr. No. 9999777742 | 9 | NIL | 9 | 9 | NIL | NIL |
| 9 | BUTTERFLY VALVE / 100 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF8 / EPDM / A479 TYPE 410 / PNEU.ACTUATOR Sr. No. 9999777770 Witness Sr. No. 9999777770 | 1 | NIL | 1 | 1 | NIL | NIL |
| 10 | BUTTERFLY VALVE / 100 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF8 / EPDM / A479 TYPE 410 / HAND LEVER 7 NOTCHES Sr. No. 9999777747 to 9999777749 Witness Sr. No. 9999777749 | 3 | NIL | 3 | 3 | NIL | NIL |
| 11 | BUTTERFLY VALVE / 125 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF8 / EPDM / A479 TYPE 410 / HAND LEVER 7 NOTCHES Sr. No. 9999777750 to 9999777754 Witness Sr. No. 9999777752 | 5 | NIL | 5 | 5 | NIL | NIL |
| 12 & 13 | BUTTERFLY VALVE / 150 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF8 / EPDM / A479 TYPE 410 / HAND LEVER 7 NOTCHES Sr. No. 9999777755 to 9999777758 Witness Sr. No. 9999777757 | 4 | NIL | 4 | 4 | NIL | NIL |

| Item # as per Contract/ Order | Description & Size | Quantity as per Contract / Order (Nos.) | Quantity Previously passed (Nos.) | Quantity Offered (Nos.) | Quantity Now Passed (Nos.) | Quantity Rejected (Nos.) | Quantity Balance (Nos.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 14 | BUTTERFLY VALVE / 200 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF3M / EPDM / A276/479 SS316L ST HARD /WORM GEAR BOX Sr. No. 9999777759 to 9999777764 Witness Sr. No. 9999777763 | 6 | NIL | 6 | 6 | NIL | NIL |
| 15 | BUTTERFLY VALVE / 200 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF8 / EPDM / A479 TYPE 410 / WORM GEAR BOX Sr. No. 9999777765 to 9999777766 Witness Sr. No. 9999777766 | 2 | NIL | 2 | 2 | NIL | NIL |
| 16 | BUTTERFLY VALVE / 250 / PN 10 / ASME B16.5-2017 (#150) / CI IS210 FG260+EPOXY /A351 CF8 / EPDM / A479 TYPE 410 / WORM GEAR BOX Sr. No. 9999777767 to 9999777769 Witness Sr. No. 9999777767 | 3 | NIL | 3 | 3 | NIL | NIL |
| 38 | CHECK VALVE / 50 / PN 16 / ASME B16.5-2017 (#150) / SGI DIN1693 GGG40+EPOXY / A351 CF8 /EPDM Sr. No. C999308824 to C999308825 Witness Sr. No. C999308824 | 2 | NIL | 2 | 2 | NIL | NIL |
| 42 | CHECK VALVE / 150 / PN 16 / ASME B16.5-2017 (#150) / SGI DIN1693 GGG40+EPOXY / A351 CF8 /EPDM Sr. No. C999308831 to C999308832 Witness Sr. No. C999308832 | 2 | NIL | 2 | 2 | NIL | NIL |